| SPECIFICATION REFERENCE | SE_«SalesEnquiry_EnquiryNo»«Special_User:» |
| --- | --- |

Pyrocel Limited

Burnbank House

Balliol Business Park West

Benton Lane

Newcastle upon Tyne

NE12 8EW

01670 70 70 70 (option 1 then option 1)

sales@pyrocel.co.uk

«SalesEnquiry_CustomerName»

«SalesEnquiry_CustomerAddress1»

«SalesEnquiry_CustomerAddress2»

«SalesEnquiry_CustomerAddress3»

«SalesEnquiry_CustomerAddress4»

«SalesEnquiry_CustomerPostCode»

| FAO |  | INSTALLATION ADDRESS |
| --- | --- | --- |
| «SalesEnquiry_SiteContactName» |  | «SalesEnquiry_SiteName» |
| DATE |  | «SalesEnquiry_SiteAddress1» |
| Tuesday, 23 June 2026 |  | «SalesEnquiry_SiteAddress2» |
| PREPARED BY |  | «SalesEnquiry_SiteAddress3» |
| «SalesEnquiry_Salesman» |  | «SalesEnquiry_SiteAddress4» |
| PYROCEL CONTACT |  | «SalesEnquiry_SitePostCode» |
| «SalesEnquiry_PreSalesAnalysis» |  |  |

Dear «SalesEnquiry_SiteContactDearName»

With reference to your enquiry, we are pleased to submit this specification and quotation for the following:

- «SalesEnquiry_TypeOfWork» - «SalesEnquiry_SystemType» System - «SalesEnquiry_SiteName»

I hope this meets with your approval. If you require any further information, please do not hesitate to contact me.

Yours faithfully

«Special_SalesmanSignature»

«SalesEnquiry_Salesman» - «Special_User:»

(for Pyrocel Limited)

[Delete any section or paragraph where appropriate and remove all text section’s coloured in red italic]

SYSTEM OVERVIEW

[Indicate what modules you are quoting for by ticking the relevant box / boxes. This is how the works will be certificated]

The following specification is for the following fire alarm modules:

| Design |  | Installation |  | Commissioning & Handover |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | (including Equipment Supply) |  |

[This paragraph is for use on supply & commission proposals. Primarily, it resolves the issue of the BoQ scenario where no design standard or category is provided. Even if there is smoke detection, it may be more appropriate to indicate (commission) to M or M/L5]

In the absence of drawings and / or a fire category Pyrocel will commission your fire detection & alarm system to the fire category that is best suited for the required protection and locations. In many instances although automatic fire protection may be fitted, only the recommendations of a manual system may be met. This is how it will be certificated. Additionally, in the absence of zonal information Pyrocel will use the minimum requirements of BS 5839 Part 1 2025 to zone your fire detection & alarm system.

[This section records the information used to compile the proposal. It is the basis of design and is what order is reviewed against]

Our costs and proposals have been based on the following information only:

| TENDER DRAWING REFERENCE |  |  | # # |
| --- | --- | --- | --- |

| OTHER INFORMATION |  |  | # # |
| --- | --- | --- | --- |

| SITE SURVEY |  | DATE | ##/##/202# |
| --- | --- | --- | --- |

| ATTENDEES |  |  | # # |
| --- | --- | --- | --- |

SCOPE OF WORKS

[To be completed by system designer/estimator]

To carry out works as detailed within the following documentation.

To modify the existing fire alarm system at (insert project name) as detailed within the following documentation.

Our quotation is subject to the outcome of a pre-installation engineering survey (detailed below), to confirm that the existing panel has sufficient spare capacity and software capabilities to support the additional devices. Depending on the age and loading of the panel, it may be unable to support the proposed equipment and additional charges would apply for system upgrading. For tender purposes, we have assumed that the proposed equipment can be supported by a single existing loop and that the panel is running recent software and is not overloaded.

DESIGN

[Choose who the system has been designed by]

The system has been designed by Pyrocel to comply with the standard and category detailed below.

The system has been designed by the Customer/Other to comply with the standard and category detailed below.

[Use this paragraph where the system has been designed by Pyrocel but no risk assessment and/or fire category was provided]

In the absence of your risk assessment and/or fire category Pyrocel offer you a fire detection & alarm system designed to the standard detailed below. However, you should have this design checked by a registered fire risk assessor (such as a serving fire officer) in order that it is seen to satisfy your fire safety and fire legislative needs.

[Use this section for non-domestic property]

The system has been designed to BS 5839 Part 1 2025 Fire Detection and Alarm Systems for Buildings to design category «Special_User:».

BS 5839 Part 1 2025 FIRE DETECTION & ALARM SYSTEM DESIGN CATEGORY

| MANUAL |
| --- |
| M | Category M system designed to provide manual alarm only (call points) |

| PROPERTY |
| --- |
| P1 | Category P1 system designed to cover throughout all areas of the building |
| P2 | Category P2 system designed to cover specified parts of the building |

| LIFE |
| --- |
| L1 | Category L1 The Fire Alarm system has been designed to Category L1, BS 5839 Part 1 2025, which satisfies the requirements for a Category M system, but also incorporates automatic fire detectors throughout all areas of the building, other than a small number of specified exceptions. |
| L2 | Category L2 The Fire Alarm system has been designed to Category L2, BS 5839 Part 1 2025, which provides cover only defined parts of the building. Identical to a Category L3 system, but with the additional objective of affording early warning of fire, in specified areas of high fire risk. |
| L3 | Category L3 The Fire Alarm system has been designed to Category L3, BS 5839 Part 1 2025, which provides automatic fire detection to escape routes and all rooms opening on to escape routes. This provides occupants with early warning to the danger, before the escape routes become smoke logged. |
| L4 | Category L4 The Fire Alarm system has been designed to cover escape routes only |
| L5 | Category L5 The Fire Alarm system has been designed to cover a particular fire safety risk |

| OTHER |
| --- |
|  | HTM05-03 Hospital Technical Memorandum; Operational Provisions Part B: Fire Detection and Alarm systems |

[Use this section for domestic property]

The System has been designed to BS 5839 Part 6 2019 Fire Detection and Fire Alarm Systems for Buildings «Special_User:» category «Special_User:». (Code of practice for the design, installation and maintenance of fire detection and fire alarm systems in dwellings)

BS 5839 Part 6 2019 FIRE DETECTION & ALARM SYSTEM DESIGN CATEGORIES

| GRADE | CATEGORY |
| --- | --- |
| A | LD* |
| C | LD* |
| D1 | LD* |
| D2 | LD* |
| F1 | LD* |
| F2 | LD* |

Please refer to the relevant standard indicated for more detailed explanation of the category coverage.

In order for the required certification to be issued as indicated above, a number of variations may need to be agreed following discussion with the appropriate interested parties, as recommended by the particular standard.

The following is a schedule of design variations to the above noted standard / category as agreed and/or instructed by the customer.

[List all agreed variations. Typical examples of variations are highlighted below. If none state NONE]

| VARIATION | DETAIL |
| --- | --- |
| V-00 | None that Pyrocel is aware of at date of quotation. |
| V-01 | No ceiling void protection has been included as instructed by the customer during initial site survey. |
| V-02 | Where the system utilises remote transmission provided by the security alarm system then a series of variations to the fire alarm standards will result. A schedule of potential variations are listed below: - The 230v mains supply is not provided via an isolating device (e.g. an isolating switch fuse) reserved solely for the purpose (i.e. dedicated) and labelled ‘FIRE ALARM: DO NOT SWITCH OFF’. BS 5839 Part 1 2025 Clause 24.1.7. - The standby battery supply is not capable of sustaining the system for at least 24 hours following a power failure and thereafter transmit an alarm signal to the remote monitoring centre. BS 5839 Part 1 2025 Clause 24.3. - The power supply is not monitored and will not give fault warning conditions, at the fire alarm panel, in the event of a failure or a disconnection of any standby power. BS 5839 Part 1 2025 Clause 11.1.2 (b) - The interconnecting cable between the FAP and the signalling device is not monitored such that an open or short circuit fault will result in a fault signal (Not a fire signal) at the FAP. BS 5839 Part 1 2025 Clause 11.1.1. (i) - Interconnecting cables are not provided in fire resisting cable. BS 5839 Part 1 2025 Clause 25.2. One should also be aware that if the PSTN or LAN cable is not provided in a fire resisting cable the cable route should be provided with automatic fire detection. |

CERTIFICATION

On completion of the works, Pyrocel will provide BS 5839 Part 1 2025 and BAFE Modular certificates for the modules instructed and indicated within System Overview.

The customer should seek certification for modules undertaken by others from the appropriate module provider.

For systems where Pyrocel has been instructed to provide all modules i.e. design, installation, commissioning / handover, the system will be verified and a BAFE Certificate of Compliance will be provided on completion of works.

Where components and devices have been requested and provided for customer’s compliance with the Equality Act 2010, Pyrocel has specified such devices to meet the customer’s specific requirements and the requirements of BS 5839 Part 1 2025 Sections 16 & 17.

SYSTEM DESIGN PARTICULARS

Power Supply Units

To ensure that the system will still function during a mains failure automatic standby power is provided. This will enable the system to remain fully operational for «Special_User:» hours and still allow the audible alarms to sound for «Special_User:» minutes thereafter, with all zones in alarm.

Double Pole Isolating Switch

We would require a key operated double pole isolating switch to be fitted adjacent to the fire alarm panel, to be provided by others at no cost to Pyrocel. The electrical circuit(s) feeding the spur unit(s) relating to the fire alarm system, should be wired using fire rated cable and should be dedicated solely to the fire alarm system and serve no other systems, or equipment. This would need to be fitted prior to attendance by the Pyrocel Engineer to begin commissioning.

[Delete cable types not used allowing consideration of cause & effect. If the design is for mixed cable, then leave in both standard and enhanced types]

| Cabling |  |
| --- | --- |
| The system will utilise the following cable type: |  |
|  | Soft skin fire resistant cables meeting the ‘standard’ requirements of BS 5839 Part 1 2025 |
|  | Soft skin fire resistant cables meeting the ‘enhanced’ requirements of BS 5839 Part 1 2025 |
|  | Mineral insulated fire resistant cable meeting the ‘enhanced’ requirements of BS 5839 Part 1 2025 |
|  | Other [specify] |
|  | Not Applicable |
| Please note: |  |
|  | All containment and conduit runs are to be by others, at no cost to Pyrocel, and generally the wiring will be surface run. However, where practicable and solely at our discretion we shall endeavour to conceal the material within the fabric of the building. |
|  | Additional engineering/installation time required for rectification of any issues arising on site due to existing equipment/cabling would be chargeable. |
|  | Wooden battens/pattresses for ceiling tile fixings are to be supplied by others at no cost to Pyrocel. |
|  | We have made no allowance for builders’ works/making good. |
|  | Cables will be stripped back to walls or ceilings only. |

Network cabling between buildings will be armoured cable installed in ducts. Our quotation is based on the assumption that ducts with draw wires will be made available for this purpose.

[Delete cause and effect not used considering risk and cable type. If no information provided, default to one out all out]

| Evacuation / Cause & Effect |  |
| --- | --- |
| Sounders will be programmed to operate in the following manner: |  |
|  | Any device in any zone will cause full evacuation immediately. |
|  | Information is not available at this stage. We would request the customer to provide this information prior to commencement of the installation process. Please note that should phased evacuation be required, this may have an effect on the system wiring and cable selection and commissioning costs. |
|  | Sounders will be programmed in accordance with the customer’s cause & effect matrix. |
|  | Other [specify] |

[Delete all Sounder notification characteristics not used. If no information provided, default to: STANDARD SOUNDERS - ‘All Sounders, Sounder/Strobes and/or detection devices that incorporate sounder electronics will be commissioned with a single tone of uniform type’ VOICE ENHANCED SOUNDERS - ‘All Voice Enhanced Sounders, Sounder/Strobes and/or detection devices that incorporate voice enhanced sounder electronics will be commissioned with the following Tone and Voice notification characteristics:‘ selecting voice message ‘Attention please this is an emergency please leave the building by the nearest available exit.‘]

| Sounders will be programmed with the following notification characteristics: |  |  |  |
| --- | --- | --- | --- |
|  | All sounders, sounder/strobes and/or detection devices that incorporate sounder electronics will be commissioned with a single uniform tone (such as the standard ‘nee naw’ tone). |  |  |
|  | All voice enhanced sounders, sounder/strobes and/or detection devices that incorporate voice enhanced sounder electronics will be commissioned with the following tone and voice notification characteristics: |  |  |
|  |  | Attention tone (single tone of uniform type such as the standard ‘nee naw’ tone) |  |
|  |  | Pre-speech silence (programmable period normally set at ten seconds) |  |
|  |  | Speech message (voice message notification) programmed to transmit the following message: |  |
|  |  |  | ‘Attention please this is an emergency please leave the building by the nearest available exit.’ (female voice) |
|  |  |  | ‘An incident has been reported in this building please await further instructions.’ (female voice) |
|  |  |  | ‘This is a test message no action is required.’ (female voice) |
|  |  |  | ‘This is a fire alarm please leave the building immediately by the nearest available exit.’ (male voice) |
|  |  |  | User defined message (message to be uploaded to the flash memory of each device by Pyrocel) |

| Outputs to plant e.g. lift control, door holder control etc provided on this project will be programmed to operate in the following manner: |  |
| --- | --- |
|  | Any device in any zone will cause operation of output to all plant controls immediately. |
|  | Information is not available at this stage. We would request the customer to provide this information prior to commencement of the installation process. |
|  | Devices will be programmed in accordance with the customer’s cause and effect matrix |
|  | Other [Specify] |

Actuation Of Release Mechanisms For Doors (BS7273-4 )

Under the requirements of BS5839-1 and BS7273-4, the user or purchaser of the system (or an appointed representative of these parties, such as a consultant) should ensure that, to the extent appropriate, there is consultation, during or prior to the design of the actuation arrangements, with all relevant interested parties (e.g. the building control body and the fire alarm contractor). The information provided inform SF1760 has been used to produce the following design for the actuation of release mechanisms for electrically held-open, electronically secured, or powered doors. PLEASE NOTE: Where the category of door actuation has not been provided to Pyrocel, all doors have been assumed to be Category B (Standard Actuation).

| Door Schedule |  |  |  |  |
| --- | --- | --- | --- | --- |
| Door ref | Door Location | Door Type | Category of Actuation | Manual Release Requirements |
| 001 EXAMPLE | Main entrance | Electronically secured door | B - Standard | Green break glass |

Device Locations

All equipment installed will be located as detailed within the drawings referenced within this specification.

[Method of communications / signalling]

| Communications & Signalling |  |
| --- | --- |
| Audible Only | The system proposed is audible only and does not communicate automatically with the fire and rescue service. Summoning the fire and rescue service will require manual telephoning using the 999 emergency telephone number. |
| Intruder Signalling System | The system proposed will be connected to the alarm receiving centre (ARC) via the communication system connected to the premises existing intruder alarm system. |
| Add:Secure Essential IP SP4 IP ONLY | The system proposed will be connected to the alarm receiving centre (ARC) via a SP4 graded single path Add:Secure Essential IP. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Static IP information must be detailed within ‘Section 5’ of ‘SF1517 keyholder request form’ or provided to Pyrocel prior to installation and commissioning. Pyrocel require an RJ45 network point and single fused spur (with double pole key switch) to be installed adjacent to the installation location** |
| Add:Secure Essential Extra DP2 GPRS/GPRS | The system proposed will be connected to the alarm receiving centre (ARC) via a DP2 graded dual path Add:Secure Essential Extra. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Communication hardware requires a single fused spur (with double pole key switch) to be installed adjacent to the installation location** |
| Add:Secure Advanced DP2 IP/GPRS | The system proposed will be connected to the alarm receiving centre (ARC) via a DP2 graded dual path Add:Secure Advanced. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Static IP information must be detailed within ‘Section 5’ of ‘SF1517 keyholder request form’ or provided to Pyrocel prior to installation and commissioning. Pyrocel require an RJ45 network point and single fused spur (with double pole key switch) to be installed adjacent to the installation location** |
| Add:Secure Advanced Extra DP4 IP/GPRS | The system proposed will be connected to the alarm receiving centre (ARC) via a DP4 graded dual path Add:Secure Advanced Extra. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Static IP information must be detailed within ‘Section 5’ of ‘SF1517 keyholder request form’ or provided to Pyrocel prior to installation and commissioning. Pyrocel require an RJ45 network point and single fused spur (with double pole key switch) to be installed adjacent to the installation location** |
| CSL GradeShift Pro Fire 2 DP2 GPRS/GPRS | The system proposed will be connected to the alarm receiving centre (ARC) via a DP2 graded dual path CSL GradeShift Pro 2 Fire. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Communication hardware requires a single fused spur (with double pole key switch) to be installed adjacent to the installation location** |
| CSL GradeShift Pro 2 DP2 IP/GPRS | The system proposed will be connected to the alarm receiving centre (ARC) via a DP2 graded dual path CSL GradeShift Pro 2. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Static IP information must be detailed within ‘Section 5’ of ‘SF1517 keyholder request form’ or provided to Pyrocel prior to installation and commissioning. Pyrocel require an RJ45 network point and single fused spur (with double pole key switch) to be installed adjacent to the installation location** |
| CSL GradeShift Pro 2 DP4 IP/GPRS | The system proposed will be connected to the alarm receiving centre (ARC) via a DP4 graded dual path CSL GradeShift Pro 2. At the earliest possible date, the client must complete and return ‘SF1517 Keyholder Request Form’ via email to arc@pyrocel.co.uk. Pyrocel will process the connection and issue communication hardware to the installation team. Please Note: Static IP information must be detailed within ‘Section 5’ of ‘SF1517 keyholder request form’ or provided to Pyrocel prior to installation and commissioning. Pyrocel require an RJ45 network point and single fused spur (with double pole key switch) to be installed adjacent to the installation location** |

[Indicate location of transmission device – Please specify]

The signalling transmitter will be installed:

| Adjacent to fire alarm panel |  | Adjacent to intruder alarm panel |  |
| --- | --- | --- | --- |

[Select signals to be transmitted with respect to risk, category and standby power]

The system will transmit the following signals to the ARC:

| Fire |  | Fire & Fault |  | Fire, Fault & AC Main Failure |  |
| --- | --- | --- | --- | --- | --- |

POINTS OF CLARIFICATION / COMPLIANCE

[Add any project specific items of clarification. Examples provided]

| Please take cognisance of the following project specific points: |  |
| --- | --- |
| 1 | It is noted that the customers’ specification indicates Category L1 protection; however, there is concern that the drawings may not meet this level of protection. We would suggest the customer should consider review of these drawings prior to commencement of installation works. |
| 2 | All installation and commissioning work is to be done during normal working hours, i.e. Monday to Friday 0830 to 1700 (statutory holidays excepted). Any extension of such hours or period directly or indirectly caused by the Customer shall entitle the Installer to charge any reasonable extra costs resulting. |
| 3 | The drawings provided indicate the provision of visual alarms within the disabled toilets only. We would recommend all general toilets be provided with visual alarms as the hard of hearing may not use defined disabled toilets. We will require further instruction to provide any additional equipment. |
| 4 | Wooden battens/pattresses for ceiling tile fixings are to be supplied by others at no cost to Pyrocel. |
| 5 | The Communication & Signalling option detailed within our quotation is subject to the signalling line or RJ45 (IP) data point (for IP based solution) being ‘live’ at commissioning stage, should a re-visit be required to complete the commissioning and ARC connection works then an additional attendance cost of £300.00 will be applicable. |
| 6 | This quotation is not fully compliant with BS 7273 Part 4 2015 Actuation of release mechanisms for doors, and therefore all door control interfaces will be listed as variations. |
| 7 | Strobe devices are not currently compliant with the new EN54 Part 23 requirements and will be listed on Pyrocel commissioning certificates as a ‘variation’. |
| 8 | For Supply & Commission works the Hochiki addressable devices must be individually programmed by the installer using the Hochiki TCH-B200 ESP Programmer. This programming equipment is included within our quotation. The devices should be programmed, then installed in position with their location and associated addresses marked up on the installers as fitted drawings. These as fitted drawings must be supplied to our commissioning engineer for commissioning to begin. |
| 9 | With regards item 2 above, failure to programme or install the addressable devices or supply the marked up as fitted drawings will lead to considerable additional commissioning time with its associated costs of which you will be charged. These costs will be deemed additional costs over and above this quotation and charged at £500.00 per day or £300.00 per half day, as necessary. |
| 10 | **Pyrocel recommend communication hardware be located on or adjacent to an exterior wall to ensure both primary and secondary communication paths achieve optimum communication to the alarm receiving centre (ARC) and help reduce the risk of radio interference caused by adjacent cabling or building structure. Should ‘High Gain Aerials’ be required, they will be supplied, installed (if applicable) and commissioned in addition to this quotation. |
| 11 | # |

EQUIPMENT SPECIFICATION

The following Items have been specified as part of our quotation:

CONTROL EQUIPMENT

MANUAL CALL POINTS

AUTOMATIC DETECTION

Detectors

Bases

AUDIBLE/VISUAL WARNING DEVICES

[Please remove when using EN54 Part 23 compliant sounder/strobe, strobe devices]

Strobe devices are not currently compliant with the new EN54 Part 23 requirements and will be listed on Pyrocel commissioning certificates as a ‘variation’.

DETECTOR SELECTION AND CONFIGURATION

[This section is MANDATORY. Additional tables must be added for each detector type and each mode selected. Use the + button at the bottom right of the table to add additional tables (the + will only be visible if you click inside the table)]

Detector types and modes have been chosen in accordance with the recommendations of BS5839-1:2025 and the equipment manufacturer.

| DETECTOR TYPE 1 |  |
| --- | --- |
| Protected area / type of area |  |
| Predominant use of area |  |
| Fire phenomenon |  |
| False alarm risk(s) |  |
| Detector type |  |
| Certificated mode chosen |  |

ANCILLARY DEVICES AND INTERFACES

All connections to third Party equipment must be made prior to system commissioning. If significant delays, and or revisits, are caused by third party equipment not being ready for final testing then this may incur additional costs. It should be noted that all connections and wiring to and from, third Party equipment is to be undertaken by others at no cost to Pyrocel.

The interfaces that we have specified are to enable the switching of the following third party equipment, as per the supplied layout drawings/specification/your kit list:

| Description |  |
| --- | --- |
| S4-344XX |  |

There are additional interfaces shown on the supplied drawings which have not been allocated in the specification/by the client. The function of these interfaces would need to be identified prior to installation / commissioning.

SYSTEMS COMMISSIONED BY PYROCEL

Systems or parts supplied by the Company carry a ‘Parts & Labour’ warranty of twelve months from date of commissioning on the basis that the system will be maintained in accordance with the manufacturers recommended frequencies.

| ADDITIONAL NOTIFICATION |  |
| --- | --- |
| The proposal has been based on the following: |  |

- Working at height from Delta Deck Low Level, Peco Lift (Wind Up) 3.5m and, or Nano (Propelled) 4.5m platforms have been included, as necessary.  Any high-level access equipment to work above this height will be provided by others at no cost to Pyrocel Limited.

- Where the sounder layout design has been provided by Pyrocel, this has been carried out based on experience of designs within similar buildings. Due to variation in building acoustics and building fabrics, there can be no guarantee of audibility levels prior to installation and fitting out. Once the system is operating in its normal environmental conditions, audibility tests will be carried out, and additional sounders installed should they be required. This work however would be subject to additional costs

- Where the works are on a supply and commission basis, we have made no provision for CAD as fitted drawings or zone plan. We will provide hand marked up drawings detailing commissioning information for production of formal as fitted drawings by others

- The control equipment and field devices are provided with standard factory finishes. Any special finishes can be provided under separate proposal

- Should the above quantities of equipment be subject to change, there will be a corresponding change in the quoted amount

- Before commissioning is carried out the fire alarm system must be fault free

- Commissioning costs have been calculated based on continuous, uninterrupted working

- We would require you to provide the services of a competent electrician who is familiar with the installed system to prove the 'as fitted' drawings and in the event of any installation faults, be available for any corrective action required

- Commissioning is inclusive of audibility tests. Details will be shown on commissioning certificates of all areas which do not comply with the current standards. Should full audibility readings be required site wide, a separate quotation can be provided for these

- Commissioning is not inclusive of audibility tests.  Following receipt of an official order in respect of this, we would be pleased to carry out audibility tests as part of the commissioning and advise on any requirement for additional sounders

- All orders dispatched by carrier that do not exceed £500.00 will incur a charge for carriage

- Gent by Honeywell Vigilon device/sensor loops will only perform satisfactorily if the following criteria are met:

  - That the current control panel has a version of software compatible with the field devices and/or any other networked control panels

  - That the quantity and combination of field devices is within the loop cards load capability. (Recommended capacity)

  - That the cable used will be restricted to 1.5mm 2 cross sectional area and that the loop length does not exceed 1000 meters

  - That the loop conductors be protected from extraneous external electrical interference by way of an earth screen. It should be noted that the information detailed above should be available PRIOR to any design certificate, intended to be BS 5839 Part 1 2025 compliant, being issued

- Where no design certificate exists then it would be preferable that the information be gathered before the installation commences to ensure that the installation as planned falls within the parameters detailed above

- We would therefore strongly advise that a Pyrocel pre-installation engineering survey be undertaken where the following tests will be undertaken and results reported

- The control panel will be interrogated to ascertain the software version in current use. This will be compared against the proposed equipment being added to the system and compatibility confirmed or required upgrade reported

- The existing system configuration will be downloaded and the loop load calculated. The loop loading will be recalculated including the additional proposed equipment and the predicted loop loading reported as a percentage of full load

- The system will be powered down and the resistance of the loop negative conductor measured

- The existing loop length and available additional cabling capacity reported

- The measured negative conductor resistance will be seen as indicative of the positive conductor resistance as this cannot be measured

- The earth screen loop resistance will be measured and we will interpret the result and ATTEMPT to confirm a continuous earth screen around the loop

- We have not included for the installation of fire stopping of any penetrations that we make to fire compartments.  Any fire stopping required would need to be done by a specialist contractor at no cost to Pyrocel.

- For the purposes of this quotation it has been assumed that there is no asbestos containing material in the areas of the proposed works.  Should this not be the case, we must be informed before works commence in order that an alternative strategy can be employed and any additional costs calculated and quoted for.

- Where the system utilises transmission provided by the security alarm system then a series of variations to the fire alarm standards will result. A schedule of potential variations are listed below:

- The 230v mains supply is not provided via an isolating device (e.g. an isolating switch fuse) reserved solely for the purpose (i.e. dedicated) and labelled ‘FIRE ALARM: DO NOT SWITCH OFF’ BS 5839 Part 1 2025 Clause 24.1.7

- The standby battery supply is not capable of sustaining the system for at least 24 hours following a power failure and thereafter transmit an alarm signal to the remote monitoring centre. BS 5839 Part 1 2025 Clause 24.3

- The power supply is not monitored and will not give fault warning conditions, at the fire alarm panel, in the event of a failure or a disconnection of any standby power. BS 5839 Part 1 2025 Clause 11.1.2 (b)

- The interconnecting cable between the FAP and the signalling device is not monitored such that an open or short circuit fault will result in a fault signal (Not a fire signal) at the FAP. BS 5839 Part 1 2025 Clause 11.1.1. (i)

- Interconnecting cables are not provided in fire resisting cable. BS 5839 Part 1 2025 Clause 25.2

- Our standard terms and conditions apply and are available on request.

- All quantities have been taken from the aforementioned supplied layout drawings only, unless referenced otherwise within our quotation. Should any additional devices be required to those that have been quoted for then additional costs will apply.

- All containment and conduit runs are to be by others, at no cost to Pyrocel, and generally the wiring will be surface run.  However, where practicable and solely at our discretion we shall endeavour to conceal the material within the fabric of the building.

- We have assumed system demonstration/witness testing can be carried out during commissioning; it is the responsibility of the client to ensure their representative is available while our engineer is on site. Should a separate visit be required this would be chargeable at £250.00 excluding VAT for up to 4 hours on site.

- We have not allowed for base labels for detectors. The addresses are to be addressed within the fire alarm configuration only.

- We have assumed that all cupboards with an area of less than 1m² do not contain high-risk items such as boilers or ignition sources unless otherwise specified. If any additional detection devices are required to protect high-risk cupboards, additional costs will apply.

END OF SPECIFICATION